## Table 1
Interim Life Safety Measures Pre-Assessment Form
| Risk Value Table |  |  | Critical Location Value Table
| Failure, Draining or Disabling of: |  |  | location | value
| Any one fire alarm initiating device | 1 |  | Anesthetizing location | 4 | Value Scoring Table
| Any one supervisory sprinkler device | 2 |  | Operating Rooms | 4
| Multiple sprinkler devices (more than 1 less than a whole zone) | 2 |  | Intensive care unit | 4 | Risk Value | X | Location Value | = | Risk Score
| Multiple initiating devices (more than 1 less than a whole zone) | 2 |  | Infant or Pediatric Unit | 4 | 4 |  | 2 |  | 8
| A fire alarm or sprinkler system or zone for 4 or more hours | 4 |  | Psychiatry | 4
| A fire alarm or sprinkler system or zone for less than 4 hours | 3 |  | Emergency Department | 4
| The off-site notification feature of a fire alarm zone or system for 4 or more hours for scheduled work | 3 |  | MRI | 3 | Step 1: Insert the matching value in the orange column of the Risk Value Table as they apply to your project. (you may have multiple risks). This automatically totals in the Risk Value box of the Value Scoring Table above.
| The off-site notification feature of a fire alarm zone or system for less than 4 hours for scheduled work | 3 |  | General Patient Care Unit | 3
| Water storage tank low water or temperature alarm failure | 3 |  | Ambulatory Patient Care Area | 2 | Step 2: Insert the matching value into the orange Location Value box above using the Critical Location Value Table. Best practice is to use the highest risk location near your project. The Risk Score will be calculated for you.
| A main drain from the sprinkler system | 3 |  | Business Occupancy | 1
| A standpipe or sprinkler connection | 3 |  | Ancillary support (Business Occupancy) | 1
| A dry pipe extinguishing ystem | 3 |  | Ancillary Support (Healthcare Occupancy) | 2
| A wet pipe extinguishing system | 3 |  | Food Service Main Kitchen | 2 | Risk Score below 8 = No further action required
| All or part of an ansul system | 3 |  | Sterile Storage area (Patient Supply) | 2 | Risk Score 8 and above = ILSM Worksheet needed
| fire or smoke dampers | 3 |  | Endscopy | 3
| Any 1 visual or audible fire alarm notification devices, including speakers | 1 |  | Mechanical Room/Machine Room | 1 | Step 3: Submit your pre-assessment form to the ILSM smartsheet for Fire Marshal review
| More than 1 visual and/or audible fire alarm notifcation devices, including speakers | 3 |  | Hazardous Materials Storage | 3
| Other Risk Issues: |  |  | Heliport | 3
| Battery Operated Egress Light repair/replace/install | 2 |  | Shell Space/Construction Site | 3
| Exit Light to be installed or repaired | 2
| Inaccessbile damper | 2
| HVAC system does not shut down upon a fire alarm condition | 3
| Broken rolling or sliding doors | 3
| Broken fire or smoke doors | 2
| Penetration in fire wall | 3
| Penetration in smoke wall | 3
) | Corridor door latching problem | 2
| Compromised smoke or fire compartment | 2
| Physical barrier in an exit or egress corridor. (eg. Stairwells, doorways, corridors, etc.) | 4 | 4
| Removal of ceiling tiles for 4 or more hours in sprinklered space | 4
| Cutting metal | 1
| Welding, brazing, soldering | 2
| Smoke or fire door (or chute door) missing rating | 1
| Deck missing fire proofing | 2
| Light lens cover missing in egress path fixture | 1